Terms of Reference for the purchase of additional

diesel generator sets for the Pit substation

| Item № | List of basic data and requirements | Basic data and requirements |
| --- | --- | --- |
| 1. | Delivery location | Kumtor Gold Company CJSC, 9 Naryn highway, Balykchy, Kyrgyz Republic. |
| 2. | Client | Kumtor Gold Company CJSC |
| 3. | General provisions | The subject of these Terms of Reference is the purchase of diesel generator sets - 3 units. |
| 4. | Requirements for the equipment | - The supplied generator sets shall be new and unused. The generator sets will be operated in high altitude conditions above 4,000 m above sea level, at the temperatures from – 35 ℃ to +40 ℃. - The equipment shall meet or exceed the requirements of the technical specifications in terms of performance and energy efficiency. - All necessary user manuals and technical documentation shall be included. - Technical documentation, user manuals, or any other documents in copy form shall not be accepted. - The equipment shall comply with the quality requirements established by technical regulations, standardization documents, and state standards applicable to this type of Goods and in force in the territory of the Kyrgyz Republic, as well as with the EAEU standards. - The equipment shall comply with the safety requirements established by the applicable laws of the Kyrgyz Republic. - When supplying the equipment, the Supplier shall provide originals or duly certified copies of valid certificates of conformity and declarations of conformity to the requirements of regulatory documents for the supplied Goods. - The equipment supplied shall not be pledged, under arrest or another encumbrance. |

| 6. | Technical specifications: | 1. Diesel generator set LSM2050S3-3B 2000 1600 16V4000G LSA 53.2 6.3 kV. 2. Container type 40'HQ, 6.3 kV, 50 Hz, total output for 3 generators - 4.8 MW (for operation at 4,000 meters above sea level). 3. With ComAp IG-NTC control panel for parallel operation of generators. 3. With ComAp IM-NT control panel for parallel connection to the network (6.3 kV network). 4. With battery and charger. 5. With water heater. With heaters to maintain the container temperature. 6. With oil pump heater. 7. With pre-lubrication system for the engine. 8. With 1,000 L external fuel tank to connect to the engine and ensure easy fuel supply to the engine. 9. With automatic refueling system. 10. With heavy-duty base frame. 11. With MTU engine, 50 Hz, model 16V4000G23. 12. With Leroy Somer generator, 6.3 kV, LSA 53.2 VL 10. 13. With PLC control system for monitoring generator status. HV switchgear cabinets. Complete set of cabinets: 1. 3 sets of HV incoming cabinets, 630 A. 2. 1 set of HV incoming cabinets, 1,600 A. 3. 1 set of CT and VT cabinets (6,300/110 VAC). 4. 3 sets of ground resistance cabinets (40 Ω/min, 6.3 kV). Monitoring 1. Siemens PLC touch screen with enclosure. 2. Batteries and charger with other related accessories. Extended cabinet 1. 1 set of reinstallation cabinet. 2. Batteries and charger with other related accessories. |
| --- | --- | --- |
| 7. | Payment and delivery terms | - Payment terms: According to the agreement concluded. - The equipment shall be delivered by manufacturer to BMY within the deadlines specified by the Client. - Assembly and commissioning shall be completed within the deadlines specified by the Client. - In case of failure to comply with the deadlines, penalties shall apply. |
| 8. | Requirements for the submission of technical and other documentation for the equipment to the Client | - Upon delivery of the Goods, the Supplier shall provide the Client with the following set of documents: - Consignment notes. - Invoice. - Original certificate of conformity. - Service book. - Equipment passport. - Documents confirming the manufacturer's and/or supplier's quality guarantee. - All necessary user manuals, technical documentation, and spare parts catalogs shall be included in the package or available in electronic form. - Before shipment from the manufacturer’s plant, the equipment shall be tested in the presence of the Client’s technical specialists. |
| 9. | Warranty period | The Supplier shall provide a warranty period for the purchased equipment in accordance with the manufacturer's terms and conditions. |
| 10. | Commissioning | 1. All costs for additional work identified during the equipment inspection shall be borne by the Supplier. 2. During commissioning and start-up and adjustment operations, the manufacturer's representative shall be present. |
| 11. | Quality evaluation criteria | 1. After commissioning, the generator set shall be evaluated during the warranty period. Evaluation results shall comply with the manufacturer's specifications. 2. In case of any non-compliance with the stated requirements, the Supplier shall bear all costs for its elimination. |
| 12. | Confidentiality | Transaction data shall be confidential. The Contractor shall be liable for disclosure to third parties. |
| 13. | Environmental requirements | The equipment shall comply with the environmental requirements established by the applicable laws of the Kyrgyz Republic. |
| 14. | Safety | The equipment shall comply with the safety requirements established by the applicable laws of the Kyrgyz Republic. |